Concept for the UPScode II
Serial Interface Protocol

Concept for the UPScode II
Serial Interface Protocol

Document number 1002889
Revision J
19 January 2004 by JE

Contents

© Copyright 2004

The contents of this manual are the copyright of
the publisher and may not be reproduced (even
extracts) unless permission granted.
Every case has been taken to ensure the
accuracy of the information contained in this
document, but no liability can be accepted for any
errors or omission. The right to make
design modifications is reserved.
# General
A UPS usually has the capability to indicate the status of operation via potential free contacts. The contacts can be indicating conditions such as: utility failure, bypass active or general alarm. The information transmitted is however quite limited.

This document describes the UPScode II interfacing protocol via RS232 line. The interface protocol consists of automatic status message transmissions, UPS status reports transmission upon request and other related commands. The interface can operate locally with a computer or remotely via modem with a monitoring center.

This is also a general description of the concept and syntax of the UPScode protocol, which is independent of the UPS type or model. It is intended as a guide and concept specification that helps the programmers of both ends of the communication to implement the communication between a power system and any computer based system utilizing the communication possibilities provided within the concept. Each implementation of this protocol in a product is a subset of the commands and messages described here.

Further development of the described protocol may bring additional commands and messages to the protocol, but these will implemented in a way that does not conflict with the examples provided in this document.

Any information in this document related to specific products is believed accurate at the date of this document, but are subject to change in future revisions of each product. Separate detailed documentation for each product is available.

# Interface protocol specifications
The serial interface protocol defines the format of UPScode commands and messages. The communication and operational parameters are also specified. The more specific description about syntax of the status messages and the values can be found from Appendix B.

## Communication parameters
The RS232 port has the following format:

Baud rate:	1200
Data bits:	8
Parity:	none
Start:	1 bit
Stop:	1 bit
Handshake:	Xon/Xoff
## Operation parameters
The operational parameters are:

Operation Mode:	standard / modem
Line Terminator:	cr+lf on output, cr on input

## Commands to the UPS
The UPS can accept several commands from the host computer or from the alarm center.

Commands to the UPS can consist of one or two parts. The first part (first row) is the command. It is 4 ASCII characters followed by Line Terminator. The first two characters are always UP (Ups) and the other two the mnemonic of the specific command.

If a command contains second part (second row), it is para­meter connected to the command. It consists of ASCII charac­ters followed by Line Terminator. The number of characters is not fixed.

## Status messages
All status messages consist of 2 parts. The first part (first row) is the general status identification label. It is 4 ASCII characters followed by Line Terminator. The first two ASCII characters are always ST (STatus) and the other two the mnemonic of the status. The second part (second row) is a detailed condition code. It consists of two ASCII characters followed by Line Terminator.

The status message with condition code 00 indicates that the indicated status condition does not exist any more. This type of status message is sent one time to indicate end of the condition.

The condition codes are specific to a UPS type. They are used to give more detailed information about the condition of the UPS. They can be either mnemonic or numeric.

## Measurement messages
The UPS measurement data consist of various measurements and calculated results of them. All of them consist of two parts.

The first part (first row) is the title of the measurement. It consists of 5 ASCII characters followed by Line Terminator. The first character is always M (Measurement) the other four is a mnemonic description of the measurement.
The second part (second row) is the actual value of the measurement. It is presented in 7 ASCII characters with decimal dot and 2 decimals followed by Line Terminator. The possible negative polarity prefix is given as first charac­ter. The examples of the output are: 0220.00(cr), -022.00(cr).

The number of the measurements in UPS measurement data depends on the UPS type and configuration and its environment monitoring capability. The length of the Status Report is therefore variable. The format of a measurements is always the same.

## Nominal value messages
The UPS nominal value and operating limit messages consist of two parts also. The first part (first row) is the title of the value. It consists of 5 ASCII characters followed by Line Terminator. The first character is always N (Nominal) the other four is a mnemonic description of the value.

The second part (second row) is the actual value. It is presented in 7 ASCII characters with decimal dot and 2 decimals followed by Line Terminator. The possible negative polarity prefix is given as first character. The examples of the output are: 0220.00(cr), -022.00(cr).

These values are helpful for example when scaling the output for a graphical presentation of the measurement values.

# Commands for ups status control and identification
The following commands are used when checking a status or getting an identification information of the unit. By means of these commands (except the UPSN command in some units), an operation of the UPS or data stored in the memory of the unit cannot be changed.

## Status report
### Automatic status messages
The UPS status messages are automatically transmitted (if automatic status messages are enabled) when the status of the UPS or remaining back up time changes. The following is the description of the status messages with descriptions on their generation in the UPS. A particular message is used only in a UPS system were the condition indicated can occur.

Status message	Description
STOK(cr)(lf) xx(cr)(lf)	UPS ON / OK xx: 00 NORMAL OPERATION 11 ABNORMAL OPERATION	Indicates the condition of the UPS. Normal means that utility is ok, battery is ok and UPS is in its normal state.
STUF(cr)(lf) xx(cr)(lf)	UTILITY FAILURE xx: 00 UTILITY OK 11 BATTERY OPERATION	Utility failure has occurred. UPS is protecting the load by using power from the batteries.
STBO(cr)(lf) xx(cr)(lf)	BATTERY OPERATION xx: 00 LINE OPERATION 11 BATTERY OPERATION	Utility failure has occurred. UPS is protecting the load by using power from the batteries. This message is used only with stand-by units instead of STUF message.
STBL(cr)(lf) xx(cr)(lf)	LOW BATTERY VOLTAGE xx: 00 BATTERY OK 11 BATTERY LOW	UPS has been using power from the batteries and battery voltage has decreased to the critical point.
STBP(cr)(lf) xx(cr)(lf)	UPS BYPASSED xx: 00 UPS ON-LINE 11 UPS BYPASSED	The load is supplied from the mains. UPS is not protecting the load.
STBM(cr)(lf) xx(cr)(lf)	BATTERY MANAGEMENT xx: CH CHARGING DI DISCHARGING FT FLOATING RS RESTING	The advanced battery management (ABMTM) status. This message is used only with UPSs with ABM capability.
STLR(cr)(lf) xx(cr)(lf)	LINE REGULATION xx: NO NORMAL, STRAIGHT THROUGH SD STEP DOWN, BUCK SU STEP UP, BOOST DU STEP UP, DOUBLE BOOST	The line regulation status. This messages is used only with UPSs with line regulation capability.

The following two messages are transmitted when the condition occurs. If there are several alarms at the same time, the messages are sent one after another. There are two levels that indicate the severity of the problem as judged by the diagnostic capability of the firmware in the UPS in question:

STAT(cr)(lf) xx(cr)(lf) / STMF(cr)(lf) xx(cr)(lf)	ATTENTION REQUIRED ON UPS CONDITION CODE / UPS MALFUNCTION. IMMEDIATE ATTENTION CONDITION CODE / xx: 00 NONE (in some units, this is sent when there is not active conditions) AC AUXILIARY CONTACT FAILURE BA BATTERIES DISCONNECTED BC BACKFEED CONTACT FAILURE BD ABNORMAL BATTERY DISCHARGE BF BATTERY FUSE FAILURE BL BATTERY LOW LIMIT BO BATTERY OVER VOLTAGE BP BYPASS FUSE FAILURE BR ABNORMAL BATTERY RECHARGE BT BATTERY OVER TEMPERATURE BX BYPASS UNAVAILABLE	UPS condition is not normal. Operator attention or service may be required. / UPS has serious malfunction. UPS shutdown and service is required.

BY BATTERY FAILURE CE CONFIGURATION ERROR CM BATTERY CONVERTER FAILURE CT CABINET OVER TEMPERATURE DO DC OVER VOLTAGE DU DC UNDER VOLTAGE EP EMERGENCY POWER OFF FF FAN FAILURE FH LINE FREQUENCY HIGH FL LINE FREQUENCY LOW FT FILTER OVER TEMPERATURE GF GROUND FAILURE HT CHARGER OVER TEMPERATURE IB INTERNAL DATA BUS FAILURE IF INVERTER FUSE FAILURE IM INVERTER FAILURE IO INVERTER OVER VOLTAGE IP INTERNAL POWER SUPPLY FAILURE IT INVERTER OVER TEMPERATURE IU INVERTER UNDER VOLTAGE IV INVERTER OFF LR LOSS OF REDUNDANCY NF NEUTRAL FAULT OD UPS NOT SUPPLYING LOAD OF OSCILLATOR FAILURE OL OVERLOAD OR REDUNDANCY OVERLOAD OV ABNORMAL OUTPUT VOLTAGE OW OUTPUT FAILURE PB PARALLEL BUS FAILURE PE PHASE ROTATION ERROR RE RECTIFIER OFF RF RECTIFIER FUSE FAILURE RM RECTIFIER FAILURE RT RECTIFIER OVER TEMPERATURE SM STATIC SWITCH FAILURE ST STATIC SWITCH OVER TEMPERATRE TT TRAFO OVER TEMPERATURE UD UPS DISABLED UO UTILITY OVER VOLTAGE US UNSYNCHRONIZED UU UTILITY UNDER VOLTAGE VE INTERNAL VOLTAGE ERROR

The following status messages are used when the system is equipped with environmental monitoring capabilities. They are transmitted only when the condition occurs.

STEA(cr)(lf) xx(cr)(lf) / STEF(cr)(lf) xx(cr)(lf)	ENVIRONMENT ATTENTION REQUIRED CONDITION CODE / ENVIRONMENT FAILURE. IMMEDIATE ATTENTION / xx: HH HUMIDITY HIGH HL HUMIDITY LOW TH TEMPERATURE HIGH TL TEMPERATURE LOW 01 ENVIRONMENT ALARM 1 02 ENVIRONMENT ALARM 2 ... 09 ENVIRONMENT ALARM 9	Environment conditions are abnormal. Operator attetion may be required. / Environment conditions are seriously abnormal. System shutdown may be required.

The following message is sent if the UPS has the capability of estimating the remaining back up time, taking into account the present load and the present charge state of the battery:

BTIME(cr)(lf) tttt.00(cr)(lf)	REMAINING BACK UP TIME tttt MINUTES	The calculated value is sent any time the UPS is supplying the load using power from the batteries. The message is repeated every time the minute value changes. Some units can also give (on request) the BTIME estimate during line operation when the UPS is supplying the load. / If the back up time can not be calculated, 9999 will be transmitted.

The BTIME value will always be the last value sent from any UPS by the UPSS command and when the messages are transmitted automatically.

### Show status
All presently valid status messages as described in 3.1.1 can be requested by sending the command:

Command	Description
UPSS(cr)	SHOW STATUS

Example of response from UPS:

Status response	Comment
STOK(cr)(lf) 11(cr)(lf)	UPS ON / OK 11 ABNORMAL OPERATION
STUF(cr)(lf) 11(cr)(lf)	UTILITY FAILURE 11 BATTERY OPERATION
STBL(cr)(lf) 00(cr)(lf)	LOW BATTERY VOLTAGE 00 BATTERY OK
STBP(cr)(lf) 00(cr)(lf)	UPS BYPASSED 00 UPS ON-LINE
STBM(cr)(lf) DI(cr)(lf)	BATTERY MANAGEMENT DI DISCHARGING
STAT(cr)(lf) US(cr)(lf)	ATTENTION REQUIRED US UNSYNCHRONIZED
BTIME(cr)(lf) 0008.00(cr)(lf)	REMAINING BACK UP TIME 8 MINUTES

## UPS status and measurements
The complete UPS status report can be requested by sending the command:

Command	Description
UPDS(cr)	DUMP STATUS

The UPS responds by transmitting the present status messages followed by the back up time message and the complete UPS measurement data. The status messages and back up time message are of the same form as described in 3.1.1.

The UPS measurement data consist of various measurements and calculated results of them. All of them con­sist of two parts. The first part (first row) is the title of the measurement. It has 5 ASCII characters followed by Line Terminator. The first character is always M (Measurement) the other four is a mnemonic description of the measurement.

The second part (2nd row) is the actual value of the measurement. It is presented in 7 ASCII char­acters with decimal dot and 2 decimals followed by Line Terminator. The possible negative polarity prefix is given as first charac­ter. The examples of the output are: 0220.00(cr)(lf), -022.00(cr)(lf).

An example of an actual output is presented in the following. The example contains messages in the format they would appear, if a system would have all the measuring capabilities implied.

Title	Description
STOK(cr)(lf) 00(cr)(lf)	UPS ON / OK 00 NORMAL OPERATION
STUF(cr)(lf) 00(cr)(lf)	UTILITY FAILURE 00 UTILITY OK
STBL(cr)(lf) 00(cr)(lf)	LOW BATTERY VOLTAGE 00 BATTERY OK
STBP(cr)(lf) 00(cr)(lf)	UPS BYPASSED 00 UPS ON-LINE
STBM(cr)(lf) CH(cr)(lf)	BATTERY MANAGEMENT CH CHARGING
BTIME(cr)(lf) 9999.00(cr)(lf)	REMAINING BACK UP TIME UNKNOWN
MIUL1(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE PHASE L1 * actual measurement value
MIUL2(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE PHASE L2 actual measurement value
MIUL3(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE PHASE L3 actual measurement value
MIU12(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE L1 TO L2 actual measurement value
MIU23(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE L2 TO L3 actual measurement value
MIU31(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE L3 TO L1 actual measurement value

MIIL1(cr)(lf) yyyy.yy(cr)(lf)	INPUT CURRENT PHASE L1 * actual measurement value
MIIL2(cr)(lf) yyyy.yy(cr)(lf)	INPUT CURRENT PHASE L2 actual measurement value
MIIL3(cr)(lf) yyyy.yy(cr)(lf)	INPUT CURRENT PHASE L3 actual measurement value
MIPL1(cr)(lf) yyyy.yy(cr)(lf)	INPUT KW PHASE L1 * calculated value
MIPL2(cr)(lf) yyyy.yy(cr)(lf)	INPUT KW PHASE L2 calculated value
MIPL3(cr)(lf) yyyy.yy(cr)(lf)	INPUT KW PHASE L3 calculated value
MISL1(cr)(lf) yyyy.yy(cr)(lf)	INPUT KVA PHASE L1 * calculated value
MISL2(cr)(lf) yyyy.yy(cr)(lf)	INPUT KVA PHASE L2 calculated value
MISL3(cr)(lf) yyyy.yy(cr)(lf)	INPUT KVA PHASE L3 calculated value
MIFFF(cr)(lf) yyyy.yy(cr)(lf)	INPUT FREQUENCY actual measurement value
MBUPO(cr)(lf) yyyy.yy(cr)(lf)	BATTERY VOLTAGE, POSITIVE actual measurement value
MBUNE(cr)(lf) yyyy.yy(cr)(lf)	BATTERY VOLTAGE, NEGATIVE actual measurement value
MBUUU(cr)(lf) yyyy.yy(cr)(lf)	BATTERY VOLTAGE actual measurement value
MBIPO(cr)(lf) yyyy.yy(cr)(lf)	BATTERY CURRENT, POSITIVE actual measurement value
MBINE(cr)(lf) yyyy.yy(cr)(lf)	BATTERY CURRENT, NEGATIVE actual measurement value
MBIII(cr)(lf) yyyy.yy(cr)(lf)	BATTERY CURRENT actual measurement value
MBCH1(cr)(lf) yyyy.yy(cr)(lf)	BATTERY CHARGE STATE IN % calculated value
MLUPO(cr)(lf) yyyy.yy(cr)(lf)	DC VOLTAGE, POSITIVE actual measurement value
MLUNE(cr)(lf) yyyy.yy(cr)(lf)	DC VOLTAGE, NEGATIVE actual measurement value
MLUUU(cr)(lf) yyyy.yy(cr)(lf)	DC VOLTAGE actual measurement value
MPUL1(cr)(lf) yyyy.yy(cr)(lf)	BYPASS VOLTAGE PHASE L1 * actual measurement value
MPUL2(cr)(lf) yyyy.yy(cr)(lf)	BYPASS VOLTAGE PHASE L2 actual measurement value
MPUL3(cr)(lf) yyyy.yy(cr)(lf)	BYPASS VOLTAGE PHASE L3 actual measurement value
MOUL1(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT VOLTAGE PHASE L1 * actual measurement value
MOUL2(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT VOLTAGE PHASE L2 actual measurement value
MOUL3(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT VOLTAGE PHASE L3 actual measurement value
MOU12(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT VOLTAGE L1 TO L2 actual measurement value
MOU23(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT VOLTAGE L2 TO L3 actual measurement value
MOU31(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT VOLTAGE L3 TO L1 actual measurement value
MOIL1(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT PHASE L1 * actual measurement value
MOIL2(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT PHASE L2 actual measurement value
MOIL3(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT PHASE L3 actual measurement value

MOIP1(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT (PEAK) PHASE L1 * actual measurement value
MOIP2(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT (PEAK) PHASE L2 actual measurement value
MOIP3(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT (PEAK) PHASE L3 actual measurement value
MOPL1(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT KW PHASE L1 * calculated value
MOPL2(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT KW PHASE L2 calculated value
MOPL3(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT KW PHASE L3 calculated value
MOSL1(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT KVA PHASE L1 * calculated value
MOSL2(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT KVA PHASE L2 calculated value
MOSL3(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT KVA PHASE L3 calculated value
MUTE1(cr)(lf) yyyy.yy(cr)(lf)	UPS TEMPERATURE (C) actual measurement value
METE1(cr)(lf) yyyy.yy(cr)(lf)	ENVIRONMENT TEMPERATURE SENSOR 1 actual measurement value
METE2(cr)(lf) yyyy.yy(cr)(lf)	ENVIRONMENT TEMPERATURE SENSOR 2 actual measurement value
MERH1(cr)(lf) yyyy.yy(cr)(lf)	ENVIRONMENT HUMIDITY SENSOR 1 actual measurement value
MERH2(cr)(lf) yyyy.yy(cr)(lf)	ENVIRONMENT HUMIDITY SENSOR 2 actual measurement value
MECO1(cr)(lf) yyyy.yy(cr)(lf)	ENVIRONMENT CONTACT 1 actual measurement value
MECO2(cr)(lf) yyyy.yy(cr)(lf)	ENVIRONMENT CONTACT 2 actual measurement value
MDI01(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT CURRENT ON DISTRIBUTION 01 actual measurement value
MOFFF(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT FREQUENCY actual measurement value

* Single phase UPS is considered to be working on phase L1

Note. The MOFFF measurement value will always be the last value sent from any UPS by the UPDS command.

## Battery status
Some systems are capable of sending the additional measurements and data of the batteries. They can be requested by the following command:

Command	Description
UPBS(cr)	BATTERY STATUS

UPS responds by sending the temperature, installation dates, and calculated ageing indexes of the internal and external batteries installed. The whole response is always sent regardless of amount of data available.

Title	Description
MBTE1(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 1 (C) actual measurement value
MBIN1(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 1 calculated value
BDAT1(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 1 quarter and year
MBTE2(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 2 (C) actual measurement value
MBIN2(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 2 calculated value
BDAT2(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 2 quarter and year
MBTE3(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 3 (C) actual measurement value
MBIN3(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 3 calculated value
BDAT3(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 3 quarter and year
MBTE4(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 4 (C) actual measurement value
MBIN4(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 4 calculated value
BDAT4(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 4 quarter and year
MBTE5(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 5 (C) actual measurement value
MBIN5(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 5 calculated value
BDAT5(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 5 quarter and year
MBTE6(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 6 (C) actual measurement value
MBIN6(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 6 calculated value
BDAT6(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 6 quarter and year
MBTE7(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 7 (C) actual measurement value
MBIN7(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 7 calculated value
BDAT7(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 7 quarter and year
MBTE8(cr)(lf) yyyy.yy(cr)(lf)	BATTERY TEMPERATURE 8 (C) actual measurement value
MBIN8(cr)(lf) yyyy.yy(cr)(lf)	BATTERY AGEING INDEX 8 calculated value
BDAT8(cr)(lf) yQyy(cr)(lf)	BATTERY INSTALLATION DATE 8 quarter and year

## UPS nominal values and limits
The complete report of the UPS nominal values and operating limits can be requested by sending the command:

Command	Description
UPDV(cr)	DUMP VALUES

The UPS responds by transmitting the values of nominal electrical parameters and applicable limit. The number of the nominal values and limits depends on the UPS type and configuration and its environment monitoring capability. The length of the Nominal Values Report is therefore variable. The format is always the same.

These values give information of the range of values to be expected. Internal logic of the UPS may use other limits to initiate control actions and diagnostic alarms as necessary.

Title	Description
NIUNN(cr)(lf) yyyy.yy(cr)(lf)	INPUT VOLTAGE NOMINAL value
NIUHH(cr)(lf) / yyyy.yy(cr)(lf)	INPUT VOLTAGE MAXIMUM / value
NIULL(cr)(lf) / yyyy.yy(cr)(lf)	INPUT VOLTAGE MINIMUM / value
NIINN(cr)(lf) yyyy.yy(cr)(lf)	INPUT CURRENT NOMINAL value
NIIHH(cr)(lf) yyyy.yy(cr)(lf)	INPUT CURRENT MAXIMUM value
NIPNN(cr)(lf) yyyy.yy(cr)(lf)	INPUT KW NOMINAL value
NIPHH(cr)(lf) yyyy.yy(cr)(lf)	INPUT KW MAXIMUM value
NISNN(cr)(lf) yyyy.yy(cr)(lf)	INPUT KVA NOMINAL value
NISHH(cr)(lf) yyyy.yy(cr)(lf)	INPUT KVA MAXIMUM value
NBUNN(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY VOLTAGE NOMINAL / value
NBUHH(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY VOLTAGE MAXIMUM / value
NBULL(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY VOLTAGE MINIMUM / value
NBIHH(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY CHARGING CURRENT MAXIMUM / value
NBILL(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY DISCHARGING CURRENT MAXIMUM / value
NBAHN(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY NOMINAL CAPACITY (Ah) / Value
NOUNN(cr)(lf) / yyyy.yy(cr)(lf)	OUTPUT VOLTAGE NOMINAL / Value
NOUHH(cr)(lf) / yyyy.yy(cr)(lf)	OUTPUT VOLTAGE MAXIMUM / Value
NOULL(cr)(lf) / yyyy.yy(cr)(lf)	OUTPUT VOLTAGE MINIMUM / value
NOINN(cr)(lf) / Yyyy.yy(cr)(lf)	OUTPUT CURRENT NOMINAL / Value
NOIHH(cr)(lf) / yyyy.yy(cr)(lf)	OUTPUT CURRENT (RMS) MAXIMUM / Value
NOPNN(cr)(lf) / yyyy.yy(cr)(lf)	OUTPUT KW NOMINAL per phase / value
NOSNN(cr)(lf) / yyyy.yy(cr)(lf)	OUTPUT KVA NOMINAL per phase / value
NBTHH(cr)(lf) / yyyy.yy(cr)(lf)	BATTERY BACK UP TIME MAXIMUM DISPLAY / value

NUTEH(cr)(lf) / yyyy.yy(cr)(lf)	UPS TEMPERATURE (C) MAXIMUM / value
NETEH(cr)(lf) / yyyy.yy(cr)(lf)	ENVIRONMENT TEMPERATURE MAXIMUM / value
NETEL(cr)(lf) / yyyy.yy(cr)(lf)	ENVIRONMENT TEMPERATURE MINIMUM / Value
NERHH(cr)(lf) / yyyy.yy(cr)(lf)	ENVIRONMENT HUMIDITY MAXIMUM / value
NERHL(cr)(lf) / Yyyy.yy(cr)(lf)	ENVIRONMENT HUMIDITY MINIMUM / value
NOFHH(cr)(lf) / Yyyy.yy(cr)(lf)	OUTPUT FREQUENCY MAXIMUM / value
NOFLL(cr)(lf) yyyy.yy(cr)(lf)	OUTPUT FREQUENCY MINIMUM value

Note. The NOFLL value will always be the last value sent from any UPS by the UPDV command.

## UPS command list
This command gives a listing of the supported UPScode commands.

Command	Description
UPCL(cr)	UPS COMMAND LIST

The UPS responds by sending a list of the commands recognized by UPS in question. An example of an actual output is presented in the following.

UPS response
UPCD(cr)(lf)
UPDA(cr)(lf)
UPDS(cr)(lf)
UPDV(cr)(lf)
UPEA(cr)(lf)
UPHU(cr)(lf)
UPPC(cr)(lf)
UPPD(cr)(lf)
UPPF(cr)(lf)
UPPH(cr)(lf)
UPPM(cr)(lf)
UPPN(cr)(lf)
UPPU(cr)(lf)
UPRL(cr)(lf)
UPRP(cr)(lf)
UPSD(cr)(lf)
UPSL(cr)(lf)
UPSN(cr)(lf)
UPSP(cr)(lf)
UPSS(cr)(lf)
UPTP(cr)(lf)
UPCL(cr)(lf)

## UPS service log
### Dump service log
The history report of alarm conditions of the UPS is available with this command.

Command	Description
UPSL(cr)	UPS SERVICE LOG

The response from the UPS is an ASCII dump which contents may vary according to the UPS series. Two examples of an actual output are presented in the following.

The UPS responds by sending the 99 last alarm conditions of the unit:

UPS response
DD.MM.YY HH:MM	31 CHARACTERS MAXIMUM(cr)(lf)
...
DD.MM.YY HH:MM	OLDEST ALARM(cr)(lf)

The UPS which does not have real time capability responds by sending the eigth last alarm conditions of the UPS:

UPS response
ACSL(cr)(lf)
DDDd HH:MM:SS	31 CHARACTERS MAXIMUM(cr)(lf)
...
DDDd HH:MM:SS	OLDEST ALARM(cr)(lf)
END(cr)(lf)

The newest alarm is sent first and the oldest alarm is sent last. Times are relative to the next (newer) alarm:
- first (newest) alarm: time from the alarm to the current moment
- other alarms: time from the alarm to the next (newer) alarm
- ‘time unknown’ is sent if the unit has been shut off between the alarm conditions
- ‘>285 days’ is given in front of the alarm when time between the alarms exceeds 285 days

### Reset service log
The following command will initialize the service log in the non-volatile memory of the unit:

Command	Description
UPRL(cr) RESSERVLOG(cr)	RESET SERVICE LOG Security code

The ten character security code ensures, that the initialization is not done by mistake, when the interface is operated manually through a terminal or by line noise.

## Identification commands
### UPS type
The UPS type information is requested by sending the command:

Command	Description
UPTP(cr)	UPS TYPE

The unit responds by sending a string identifying the UPS type. Some units can also send a firmware revision of the UPS after the type string.

Title	Description
NNAME(cr)(lf) pppp(cr)(lf)	UPS TYPE pppp is an ASCII string of max. 20 characters.

### UPS ID
The identification information is requested by sending the command:

Command	Description
UPID(cr)	UPS ID

The unit responds by sending an ID string of the UPS.

Title	Description
ACID(cr)(lf) pppp(cr)(lf)	UPS ID pppp is an ASCII string of max. 10 characters.

### Serial number
Command	Description
UPSN(cr) ssss(cr)	SERIAL NUMBER Identification of the unit (max 20 characters)

The serial number of the unit can be set with this command (the setting is not possible with some UPS models but the string stored in memory can be requested by 0(cr) argument).

ssss is the string in ASCII that contains the serial number of the unit. The string is stored in non-volatile memory of the unit. The rightmost digits in serial number are the significant ones.

The UPS will acknowledge the command by transmitting:

Title	Description
ACSN(cr)(lf) ssss(cr)(lf)	SERIAL NUMBER ssss is an ASCII string (max 20 characters).

### Part number
Command	Description
UPPN(cr) 0(cr)	PART NUMBER

The part number of the unit can be requested with this command followed by dummy argument 0(cr) given for compatibility with previous firmware.

The UPS will acknowledge the command by transmitting:

Title	Description
ACPN(cr)(lf) ssss(cr)(lf)	PART NUMBER ssss is an ASCII string (max 16 characters).

ssss is the string in ASCII (max 16 characters) that contains part number of the unit. The string is stored in non-volatile memory of the unit. The rightmost digits in part number are the significant ones.

# Commands for changing ups data and operation
There are also commands which are used to change the operational parameters of the UPS or to store information in the memory of the unit. These commands include the following:

## Shutdown and startup commands
### Shutdown delay
The shutdown delay time is the time from the issue of a shutdown command either by hardware contact or UPScode command, to the shutdown of the UPS output.

The delay can be viewed or set by UPSD command. The following formats of the command are possible:

Command	UPS response	Description
UPSD(cr) 0(cr)	ACSD(cr)(lf) ttt(cr)(lf)	SHUTDOWN DELAY	The present value ttt of the delay is requested.
UPSD(cr) ttt(cr)	ACSD(cr)(lf) ttt(cr)(lf)	SET SHUTDOWN DELAY ttt is the delay in seconds	The value of the delay is changed to ttt.

The second part (second row) of the command defines the command function:

- View the delay: second part is 0(cr). No change to the delay is done. The shutdown delay time presently in the memory of the UPS is transmitted in acknowledgement, where ttt is the delay in seconds.
- Set the delay: second part (ttt(cr)) is the time in seconds and the Line Terminator. The time is stored in the non-volatile memory of the unit. The new shutdown delay time is transmitted in acknowledgement.

### Conditional shutdown
Command	Description
UPPF(cr) IJHLDMGCIU(cr)	POWER DOWN UPS (DURING LINE FAILURE) Security code

The command will cause the shutdown of the UPS output voltage after a delay set by the UPSD command during input line failure. The command can be cancelled before the shut down with UPPU command. The function of the UPPF command corresponds to the hardware shutdown. The ten character security code ensures that a shutdown is not started by mistake when the interface is operated manually through a terminal or by line noise.

### Restart delay
The restart delay time is backup time that is charged into the batteries after the UPPF or a battery shutdown before re-enabling the UPS output voltage.

The delay can be viewed or set by UPRD command. The following formats of the command are possible:

Command	UPS response	Description
UPRD(cr) (cr)	ACRD(cr)(lf) ttt(cr)(lf)	RESTART DELAY	The present value ttt of the delay is requested.
UPRD(cr) ttt(cr)	ACRD(cr)(lf) ttt(cr)(lf)	SET RESTART DELAY ttt is the delay in minutes of backup time	The value of the delay is changed to ttt.

The second part (second row) of the command defines the command function:

View the delay: second part is (cr) or x(cr) where x is not a figure. No change to the delay is done. The restart delay time presently in the memory of the UPS is transmitted in acknowledgement, where ttt is the backup time in minutes.
Set the delay: second part (ttt(cr)) is the backup time in minutes and the Line Terminator. The time is stored in the non-volatile memory of the unit. The new restart delay time is transmitted in acknowledgement.

### Unconditional shutdown
Command	Description
UPPD(cr) LGGNLMDPGV(cr)	POWER DOWN UPS UNCONDITIONALLY Security code

The above command will cause the shutdown of the UPS output voltage after a delay set by the UPSD command regardless of the state of the input line status. The command can be cancelled before the shutdown with UPPU command.

The UPS will re-enable its output voltage only when UPPU command is received. If the input line voltage is “OK”, the UPS output voltage is re-enabled immediately. Otherwise, the output voltage is re-enabled after the input line voltage returns.

### Power cycle shutdown
Command	Description
UPPC(cr) IJHLDMGCIU(cr)	POWER CYCLE UPS Security code

The command will cause the shutdown of the UPS output voltage after a delay set by the UPSD command regardless of the state of the input line status. The command can be cancelled before the shut down with UPPU command. The UPS will re-enable the UPS output voltage after a delay set by the UPCD command or when the UPPU command is received, only if the input line voltage is "OK".

If the input line voltage is "failed" when the power cycle delay has expired, or when the UPPU command is received, the UPS will not re-enable the output voltage until the input line returns.

### Power cycle delay
The power cycle delay time is the time from the shutting down of the output voltage with the UPPC command until re-enabling the output voltage.

The delay can be viewed or set by UPCD command. The following formats of the command are possible:

Command	UPS response	Description
UPCD(cr) 0(cr)	ACCD(cr)(lf) ttt(cr)(lf)	POWER CYCLE DELAY	The present value ttt of the delay is requested.
UPCD(cr) ttt(cr)	ACCD(cr)(lf) ttt(cr)(lf)	SET POWER CYCLE DELAY ttt is delay in seconds	The value of the delay is changed to ttt.

The second part (second row) of the command defines the command function:
- View the delay: second part is 0(cr). No change to the delay is done. The power cycle delay time presently in the memory of the UPS is transmitted in acknowledgement, where ttt is the delay in seconds.
- Set the delay: second part (ttt(cr)) is the time in seconds and the Line Terminator. The time is stored in the non-volatile memory of the unit. The new power cycle delay time is transmitted in acknowledgement.

### Startup command
Command	Description
UPPU(cr)	CANCEL POWER DOWN COMMAND

This command cancels the UPPF, UPPC and UPPD commands during shutdown delay and re-enables the UPS output voltage immediately when the input line voltage is “OK”.

### Shutdown of output channel
Shutdown and restart of the PCU's output channel can be carried out by UPLC command. The following formats of the command are possible:

Command	UPS response	Description
UPLC(cr) 0(cr)	ACLC(cr)(lf) C01(cr)(lf) C02(cr)(lf)	OUTPUT CHANNEL LIST	A listing of the output channels that can be controlled with the UPLC command is requested.
UPLC(cr) Cnn(cr)	ACLC(cr)(lf) CnnTttttt(cr)(lf)	OUTPUT CHANNEL RESTART DELAY Cnn is number of the channel	The present value ttttt of the delay is requested.
UPLC(cr) CnnT0(cr)	ACLC(cr)(lf) CnnT0(cr)(lf)	RESTART OUTPUT CHANNEL delay is 0	The output channel is re-enabled if it has been off
UPLC(cr) CnnTttttt(cr)	ACLC(cr)(lf) CnnTttttt(cr)(lf)	SHUTDOWN AND RESTART ttttt is delay in minutes (1-65534) to be off	The output channel is shut off after UPSD delay. Value of the restart delay is changed to ttttt. Restart after ttttt minutes.
UPLC(cr) CnnTttttt (cr)	ACLC(cr)(lf) CnnTttttt (cr)(lf)	PERMANENT SHUTDOWN ttttt is delay in minutes (65535 or more)	The output channel is shut off permanently.

The second part (second row) of the command defines the command function:

- List output channels: second part is 0(cr). No change to any parameters is done. Listing of the PCU's output channels that can be controlled is transmitted in acknowledgement.
- View the delay: second part is Cnn(cr). No change to the delay is done. The delay time left until the output channel will be re-enabled is transmitted in acknowledgement.
- Restart the output channel: second part is Cnn, followed by T (Time), the delay 0 minutes, and Line Terminator. The output channel will be re-enabled immediately if it has been off and then it will stay on permanently.The zero delay time is transmitted in acknowledgement.
- Set the delay and shutdown the output channel: second part is Cnn, followed by T (Time), the delay ttttt in minutes, and by Line Terminator. The command will cause the shutdown of the PCU's output channel #nn after the delay set by the UPSD command. ttttt is the ASCII string in minutes (1-65534) that contains time from shutting down of the output channel until re-enabling the PCU's output. Number of the channel nn must be given by two figures but the delay time can be fed by 1 to 5 characters.The new output channel restart delay time is transmitted in acknowledgement.
- Shutdown the output channel permanently: second part is Cnn, followed by T (Time), the delay 65535 minutes or more, and Line Terminator. The command will cause a permanent shutdown of the PCU's output channel after the UPSD delay. The given delay ttttt is transmitted in acknowledgement.

### Restart delay for output channel
When the loads are restarted on power up of the UPS, the restart delay of individual output channels can be set with the UPLR command. The following formats of the command are possible:

Command	UPS response	Description
UPLR(cr) Cnn(cr)	ACLR(cr)(lf) CnnDttt(cr)(lf)	UPS LOAD RESTART DELAY Cnn is number of the channel	The delay ttt left until the output channel will be re-enabled is requested.
UPLR(cr) CnnDttt(cr)	ACLR(cr)(lf) CnnDttt(cr)(lf)	SET UPS LOAD RESTART DELAY ttt is time in minutes (0-999) to delay restart	The value of the delay is changed to ttt.

The second part (second row) of the command defines the command function:

- View the delay: second part is Cnn(cr). No change to the delay is done. The delay time left until the output channel will be re-enabled is transmitted in acknowledgement. The factory default delay is 0 minutes.
- Set the delay: second part is Cnn, followed by D (Delay), the delay ttt in minutes, and by Line Terminator. The time is stored in the non-volatile memory of the unit. The new restart delay time is transmitted in acknowledgement.

## Battery self test
The following command will initiate the automatic battery condition test function of the UPS.

Command	Description
UPBT(cr) ddd(cr)	INITIATE AUTOMATIC BATTERY SELF TEST Repeat time days

The repeat time determines how often the test will be performed. If the number is 0, the automatic test function is disabled. If the repeat time is 1, the test will be carried out only one time. For any other number, the test will be carried out once immediately and then at intervals of ddd days.

If the battery condition test indicates that the battery condition is degraded, a status message for battery condition will be issued:

STAT(cr)(lf)
BY(cr)(lf)

If the battery condition is such, that there is virtually no backup time left, a malfunction status message may be seen:

STMF(cr)(lf)
BY(cr)(lf)

The above messages will be issued automatically, after the test is performed, if the automatic messages are enabled. If automatic messages are disabled, the status must be requested by the UPSS or UPDS commands. The battery condition status will remain, until a successful battery test has been performed.

## UPS self test
The self test function of the UPS can be started by the following command:

Command	Description
UPIS(cr)	INITIATE SELF TEST

The UPS responds by performing the self test if required conditions (line operation, no overload, etc) are valid.

## Parameter setting command
The operational parameters can be viewed or set by UPPM command. The following formats of the command are possible:

Command	UPS response	Description
UPPM(cr) 0(cr)	ACPM(cr)(lf) P01(cr)(lf) P02(cr)(lf) P03(cr)(lf) P04(cr)(lf) P05(cr)(lf) P06(cr)(lf) P07(cr)(lf) P08(cr)(lf) P09(cr)(lf) P13(cr)(lf) P16(cr)(lf) P18(cr)(lf) P19(cr)(lf) P20(cr)(lf) P23(cr)(lf) P24(cr)(lf) P25(cr)(lf) P26(cr)(lf) P27(cr)(lf) P28(cr)(lf) P29(cr)(lf)	PARAMETER LIST (example)	A listing of the adjustable parameters is requested.
UPPM(cr) Pmm(cr)	ACPM(cr)(lf) PmmVnn(cr)(lf)	PARAMETER VALUE Parameter	The present value nn of the parameter mm is requested.
UPPM(cr) PmmVnn(cr)	ACPM(cr)(lf) PmmVnn(cr)(lf)	SET UPS PARAMETER Parameter and operation	The parameter mm value is changed to nn.

The second part (second row) of the command defines the command function:
- List of all adjustable parameters: second part is 0(cr). No change to any parameters is done. Lists all existing parameters in the UPS.
- A parameter value: second part is Pmm(cr), where the first character is always P (Parameter) followed by the number of the parameter mm which value is requested. No change is done, but the value presently in the memory of the UPS is transmitted in acknowledgement: PmmVnn(cr), where mm is the number of the parameter and nn is the number of the operation.
- Set a parameter value: second part is Pmm, followed by V (Value), the number of the operation nn, and by Line Terminator. If the parameter number and operation value are correct, the new value for the parameter is stored in the non-volatile memory of the unit. The value of the parameter is transmitted in acknowledgement.

The operational parameters that can be viewed and set with UPPM command are:

mm	Parameter	nn	Operation
00	Programmable battery low relay signal	00 01 02 03 04	Battery low Line failure General alarm Pending shutdown Environment alarm

01	Battery size	00-	UPS specific
02	Modem communication test mode	00 01	The UPS calls to a service centre only when alarm condition occurs The UPS calls also if utility failure is detected
03	Output voltage	00-	UPS specific
04	Output frequency	00 01 02	50 Hz 60 Hz Frequency taken from the EEPROM
05	Battery low alarm level	00 01 02	Nominal voltage level Higher level Lower level
06	Synchronization window	00 01 02 03	Narrow Wide Middle size Window size taken from the EEPROM
07	Operation mode of RS232 interface	00 01	The interface operatesin startdard mode The interface operates in modem communication mode
08	Audible alarm	00 01 02	Sound ON Suppress line failure Suppress all alarms
09	Line failure alarm delay	00 01-99	Relay, buzzer & UPScode status activated immediately after failure Relay, buzzer & UPScode status activated after 1-99 seconds
10	Startup delay at line return	00 01-10	Nominal delay 1-10 s is added to nominal delay
11	Transfer sensitivity	00 01	Normal Tolerant
12	Force bypass	00 01 02 03	Normal operation Only bypass operation, inverter off Only bypass operation, inverter on No bypass operation
13	ABM functions	00 01 02 03 04	All ABM functions enabled ABM battery charging cycles disabled Battery failure alarms disabled Battery failure alarms and ABM battery charging cycles disabled No batteries (battery operation and related alarms disabled)
14	Ground failure disable	00 01	Not disabled by user Disabled by user
15	Operation of BL and LF relay signals	00 01	Normal PCU support
16	Bypass limits	00-	UPS specific
17	Manual restart
18	Frequency slew rate	00 01 02 03	Low (<0.5 Hz/s) High (2.5 Hz/s) Very high Slew rate taken from the EEPROM
19	Service modes	00 01 02 03 04 05 06	Normal operation Battery operation (backfeed relay open) Bypass operation, inverter on Bypass operation, inverter off Bypass operation, inverter on, backfeed relay open Bypass operation, inverter off, backfeed relay open Output breaker trip command
20	UPS type string	00 01	Takes the response to UPTP command from non-volatile memory Sends “UPS” and firmware revision as response to UPTP command
21	Backup time	00 01-99	Unknown batteries, BTIME always ’9999.00’ Backup time with full batteries and nominal (100%) load
22	Backup time at battery low alarm level	00-99	Backup time at battery low alarm level and nominal (100%) load

23	Efficiency optimizer mode	00 01-99	No efficiency optimizer mode Bypass must be synchronized and voltage level ok 1 - 99 min before transfer from inverter to bypass
24	Transfer acceptance	00 01	Requires synchronization Transfers also while unsynchronized
25	Operational priority during rectifier input break	00 01	On battery On bypass
26	Shutdown commands	00 01	UPScode II shutdown commands enabled UPScode II shutdown commands disabled
27	Options installed	00 01 02 03	None Output transformer installed Input filter installed Output transformer and input filter installed
28	Paralleling enable/disable	00 01 02 03 04	Single unit operation Parallel operation, unit #1 (shortest startup delay) Parallel operation, unit #2 Parallel operation, unit #3 Parallel operation, unit #4 (longest startup delay)
29	Load sharing mode	00 01	Communication cable between the parallel units connected Wireless paralleling mode (bypass disabled)
30	EL operation mode	00 01	Normal operation Unit operates in EL mode (bypass disabled)
31	Paralleling mode	00 01	Parallel for redundancy Parallel for capacity
32	Utility alarms	00 01 02 03	No utility alarms (other than line failure) Status when bypass is not available (no alarm LED and relay) Status with alarm LED and relay when rectifier input is out of the limits Status with alarm LED and relay when bypass is not available or rectifier input is out of the limits
33	Utility over voltage detection	00 01	High rectifier input voltage does not cause transfer to battery operation Transfer to battery operation when the rectifier input over voltage detected
34	Battery temperature compensation	00 01	Temperature compensated battery charging No temperature compensated battery charging
35	Bypass usage	00 01 02 03	Bypass operation and synchronization to the bypass enabled Bypass enabled but sync disabled when N + 1 parallel units in operation Bypass enabled but synchronization disabled on inverter Bypass operation and synchronization to the bypass disabled
36	Battery backup time estimation	00-	UPS specific

## Reset UPS parameters
Command	Description
UPRP(cr) RESUPSPARS(cr)	RESET PARAMETERS Security code

The command will cause the adjustable UPS parameters and delays, a phone number, and a password to be reset or set to their default values (and stored in non-volatile memory of the unit).

The ten character security code ensures that an initialization is not started by mistake when the interface is operated manually through a terminal or by line noise.

## Other Commands
### Automatic messages ON/OFF
Command	Description
UPDA(cr)	DISABLE AUTOMATIC MESSAGES (DEFAULT)
UPEA(cr)	ENABLE AUTOMATIC MESSAGES

These commands can be used to enable/disable the sending of the automatic status messages described in 3.1.1. If the automatic messages are disabled, the commands UPSS and/or UPDS must be used to get the present UPS status.

### Note fields
Information such as battery replacement date, revision level of PCBA, description of the device connected into the UPS etc. can be can be viewed or set by UPNx command. x is a running number of the note field (UPN0, UPN1, ... or UPN9) where the information will be stored. The amount of the note fields depends on the UPS type and firmware revision.

The following formats of the command are possible:

Command	UPS response	Description
UPNx(cr) 0(cr)	ACNx(cr)(lf) ssss(cr)(lf)	USER NOTE FIELD x, where x = 0…9	The present user defined string ssss is requested.
UPNx(cr) ssss(cr)	ACNx(cr)(lf) ssss(cr)(lf)	SET USER NOTE FIELD x ssss is the string defined by user, max 10 characters	The contents of the string number x is changed to ssss.

The second part (second row) of the command defines the command function:

- View the note field: second part is 0(cr). No change to the string is done. The note field presently in the memory of the UPS is transmitted in acknowledgement.
- Set the note field: second part (ssss(cr)) is the string in ASCII and the Line Terminator. The string (max 10 characters) is stored in non-volatile memory of the unit.

### Set date
The date of the internal clock of a unit can be set with the UPDT command. The following formats of the command are possible:

Command	UPS response	Description
UPDT(cr) 0(cr)	ACDT(cr)(lf) yymmdd(cr)(lf)	READ DATE	The present date setting of the UPS yymmdd is requested.
UPDT(cr) yymmdd(cr)	ACDT(cr)(lf) yymmdd(cr)(lf)	SET DATE yymmdd is a numerical date string	The date setting of the UPS is changed to yymmdd.

The second part (second row) of the command defines the command function:

- View the date: second part is 0(cr). No change to the string is done. The present date setting of the UPS is transmitted in acknowledgement.
- Set the date: second part (yymmdd(cr)) is the string in ASCII that contains the year, month, and day as a six digit numerical string, and the Line Terminator. The new date setting of the UPS is transmitted in acknowledgement.

### Set time
The date of the internal clock of a unit can be set with the UPTM command. The following formats of the command are possible:

Command	UPS response	Description
UPTM(cr) 0(cr)	ACTM(cr)(lf) hhmmss(cr)(lf)	READ TIME	The present time setting of the UPS hhmmss is requested.
UPTM(cr) hhmmss(cr)	ACTM(cr)(lf) hhmmss(cr)(lf)	SET TIME hhmmss is a numerical time string	The time setting of the UPS is changed to hhmmss.

The second part (second row) of the command defines the command function:

- View the time: second part is 0(cr). No change to the string is done. The present time of day setting of the UPS is transmitted in acknowledgement.
- Set the time: second part (hhmmss(cr)) is the string in ASCII that contains the hours, minutes, and seconds as a six digit numerical string, and the Line Terminator. The new time of day setting of the UPS is transmitted in acknowledgement.

### Alarm reset ON/OFF
Command	Description
UPR1(cr)	ALARM RESET ON
UPR0(cr)	ALARM RESET OFF

These commands can be used to reset inactive alarm conditions, silence the buzzer beepings, and perform other functions which can be done by a reset button. After the UPR1 command the UPS operates like the reset button is being pushed. The UPR0 command tells to UPS that the “reset button” is not pushed any more.

# Commands for remote operation via modem
The operation via a modem is similar to the local operation after establishing a connection. The connection is established by connecting a modem in auto answer mode to the 25-pin RS 232 port, and calling the number to which the modem is connected.

A connection, where the UPS calls a service center using the number according to the command string set by UPPH(cr) command, is also possible, but requires a setup in cooperation with the service center.

In the following are the commands which are mainly used when operating in modem communication mode.

## Telephone number set
A complete command string for the modem can be viewed or set by the UPPH command. This string is stored in the non-volatile memory of the UPS and used to command the modem to call when needed. Example: ATDT 1234567.

The following formats of the command are possible:

Command	UPS response	Description
UPPH(cr) 0(cr)	ACPH(cr)(lf) pppp(cr)(lf)	TELEPHONE NUMBER	The present command string pppp is requested.
UPPH(cr) pppp(cr)	ACPH(cr)(lf) pppp(cr)(lf)	TELEPHONE NUMBER SET Command string for modem with phone number to call, max 20 characters	The command string is changed to pppp.

The second part (second row) of the command defines the command function:
- View the command string: second part is 0(cr). No change in the command string is done. The string presently in the memory of the UPS is transmitted in acknowledgement.
- Set the command string: second part (pppp(cr)) is the ASCII string for modem with phone number to call and the Line Terminator. The string is stored in the non-volatile memory of the unit.

## Password operations
When operating in modem communication mode via the RS232 interface the UPS is set up to require a password before allowing access to the commands by which operations of the UPS can be changed (shutdown commands and delays, setting of UPS parameters, changing of phone number). However, all status messages, measurements, identification data, values of the parameters and shutdown delays can be checked without a password. In standard communication mode the password is not needed.

A password can be given or changed by UPSP command. The following formats of the command are possible:

Command	UPS response	Description
UPSP(cr) PASSWD(cr)	(no response)	GIVE PASSWORD Password to allow access to all commands, max 10 characters.	The password ‘PASSWD‘ is given.
UPSP(cr) OLD PASSWD(cr) UPSP(cr) NEW PASSWD(cr)	ACSP(cr)(lf) NEW PASSWD(cr)(lf)	CHANGE PASSWORD Old password New password	Changing the password from ‘OLD PASSWD‘ to ‘NEW PASSWD‘ in modem communication mode.
UPSP(cr) don’t care(cr) UPSP(cr) NEW PASSWD(cr)	ACSP(cr)(lf) NEW PASSWD(cr)(lf)	CHANGE PASSWORD New password	Changing the password to ‘NEW PASSWD‘ in standard communication mode.

The format of the command defines the command function:
- Giving the password: second part (PASSWD(cr)) is the password and the Line Terminator. The password is an ASCII string that is compared with the string stored in the non-volatile memory of the unit. The default value for the password is only (cr). If the password was accepted, then all commands are available until the modem connection is terminated. During a new connection the password has to be given again if needed.
- Changing the password in modem communication mode: second part (OLD PASSWD(cr)) is the old password to be changed; third part is UPSP(cr) again; fourth part (NEW PASSWD(cr)) is the new password of 10 characters maximum. If the new password includes more than 10 characters, password is not changed, and the UPS will send the old password in acknowledgement. Care should be taken to note the new password!
- Changing the password in standard communication mode (the old password is not needed): second part can be anything, for example just (cr); third part is UPSP(cr) again; fourth part (NEW PASSWD(cr)) is the new password of 10 characters maximum. If the new password includes more than 10 characters, password is not changed, and the UPS will send the old password in acknowledgement. Care should be taken to note the new password!

An example about the operation of the UPScode commands in modem communication mode before a password has been received is shown in the following table.

Commands that work normally	Read only commands 1)	Commands that are not in use
UPCL UPDS UPDV UPHU UPPN UPPU UPR0 UPR1 UPSL UPSN UPSP UPSS UPTP	UPCD UPPH UPPM UPSD	UPDA UPEA UPPC UPPD UPPF UPRL UPRP

1) The value stored in the EEPROM can be requested but cannot be changed

## Hang up connection
Command	Description
UPHU(cr)	HANG UP MODEM CONNECTION

In modem communication mode the above command will force the UPS end to hang up, and terminate the modem connection.
# Programming hints
In order to keep software compatibility between single phase and three phase UPSes as well as future UPS models, any interpreting software should ignore any unrecognized messages and should never expect all the above messages to be transmitted. Also note that all commands are in UPPER CASE.

The following is an example of how to implement a UPScode interpreting application:

Input handling:

Variables are assigned for each status condition or value of interest, and a table of the associated status messages (ST**), measurement labels (M****) and nominal values or limits (N***).

For each incoming line from the UPS, the software checks against the table for a known message and in case the label is identified, the parameter is read from the following line. In case the parameter is valid, the corresponding variable is updated.

The data in the variables can then be used to display, log or take necessary action.

Output handling:

Initially, issue the UPDV, UPDS and/or the UPSS commands to the UPS, to get all status’s and values needed. The automatic status messages from the UPS will then keep the status updated in the variables automatically. If a status received implies some action, issue a UPSS command to verify the status information. To update the measurement values, issue the UPDS command at appropriate intervals.

In case the UPS does not seem to respond, issue two (cr) characters to clear the command buffer of the UPS in case it has received spurious characters due to line noise etc.
APPENDIX A: Reserved UPScode commands
In the following is a list of the reserved UPScode commands at the moment. The set of the commands for each product is fixed and they are described in the separate detailed documents. The summary of the UPScode commands used in present products can be found in the document 1005998.

Command	Description
UPxx(cr)	xx: BS BATTERY STATUS BT INITIATE BATTERY SELF TEST CD SET POWER CYCLE DELAY CL UPS COMMAND LIST DA DISABLE AUTOMATIC MESSAGES DS DUMP STATUS DT SET DATE DV DUMP VALUES DX RESERVED EA ENABLE AUTOMATIC MESSAGES FS RESERVED HU HANG UP MODEM CONNECTION ID UPS ID IS INITIATE SELF TEST LC UPS LOAD CONTROL LR UPS LOAD RESTART DELAY Nx USER NOTE FIELD x, WHERE x = 0…9 PC POWER CYCLE UPS PD POWER DOWN UPS UNCONDITIONALLY PF POWER DOWN UPS (DURING LINE FAILURE) PH SET TELEPHONE NUMBER PM SET UPS PARAMETER PN PART NUMBER PR RESERVED PU CANCEL POWER DOWN COMMAND R0 ALARM RESET OFF R1 ALARM RESET ON RD RESTART DELAY RL RESET SERVICE LOG RM RESERVED RP RESET PARAMETERS SD SET SHUTDOWN DELAY SL SERVICE LOG SN SERIAL NUMBER SP SET PASSWORD SS SHOW STATUS ST STATUS REPORT TM SET TIME TP UPS TYPE

APPENDIX B: Syntax description of codes from UPS
The set of messages for each product is fixed and described in the document 1005998. The following information is provided only as a reference for programming interpretive software.

B.1 Status messages (4 character labels)
Title	Description
STxx(cr)(lf) aa(cr)(lf)	SYSTEM STATUS / When xx: OK ON/OK UF Utility Failure BO Battery Operation BL Battery Low BP ByPassed / aa: condition code 00 NONE, INACTIVE 11 VALID, ACTIVE / When xx: BM Battery Management / aa: condition code CH CHARGING DI DISCHARGING FT FLOATING RS RESTING / When xx: LR Line Regulation / aa: condition code NO NORMAL, STRAIGHT THROUGH SD STEP DOWN, BUCK SU STEP UP, BOOST DU STEP UP, DOUBLE BOOST / When xx: AT Attention MF MalFunction / aa: condition code 00 NONE, INACTIVE AC AUXILIARY CONTACT FAILURE BA BATTERIES DISCONNECTED BC BACKFEED CONTACT FAILURE BD ABNORMAL BATTERY DISCHARGE BF BATTERY FUSE FAILURE BL BATTERY LOW LIMIT BO BATTERY OVER VOLTAGE BP BYPASS FUSE FAILURE BR ABNORMAL BATTERY RECHARGE BT BATTERY OVER TEMPERATURE BX BYPASS UNAVAILABLE BY BATTERY FAILURE CE CONFIGURATION ERROR CM BATTERY CONVERTER FAILURE CT CABINET OVER TEMPERATURE DO DC OVER VOLTAGE

	DU DC UNDER VOLTAGE EP EMERGENCY POWER OFF FF FAN FAILURE FH LINE FREQUENCY HIGH FL LINE FREQUENCY LOW FT FILTER OVER TEMPERATURE GF GROUND FAILURE HT CHARGER OVER TEMPERATURE IB INTERNAL DATA BUS FAILURE IF INVERTER FUSE FAILURE IM INVERTER FAILURE IO INVERTER OVER VOLTAGE IP INTERNAL POWER SUPPLY FAILURE IT INVERTER OVER TEMPERATURE IU INVERTER UNDER VOLTAGE IV INVERTER OFF LR LOSS OF REDUNDANCY NF NEUTRAL FAULT OD UPS NOT SUPPLYING LOAD OF OSCILLATOR FAILURE OL OVERLOAD OR REDUNDANCY OVERLOAD OV ABNORMAL OUTPUT VOLTAGE OW OUTPUT FAILURE PB PARALLEL BUS FAILURE PE PHASE ROTATION ERROR RE RECTIFIER OFF RF RECTIFIER FUSE FAILURE RM RECTIFIER FAILURE RT RECTIFIER OVER TEMPERATURE SM STATIC SWITCH FAILURE ST STATIC SWITCH OVER TEMPERATRE TT TRAFO OVER TEMPERATURE UD UPS DISABLED UO UTILITY OVER VOLTAGE US UNSYNCHRONIZED UU UTILITY UNDER VOLTAGE VE INTERNAL VOLTAGE ERROR / When xx: EA Environment Attention EF Environment Failure / aa: condition code HH HUMIDITY HIGH HL HUMIDITY LOW TH TEMPERATURE HIGH TL TEMPERATURE LOW 01 ENVIRONMENT ALARM 1 02 ENVIRONMENT ALARM 2 ... 09 ENVIRONMENT ALARM 9
ASxx(cr)(lf) aa(cr)(lf)	RELAY STATUS (UPScode I, see Appendix C) / Where xx: OK ON/OK BP ByPassed UF Utility Failure BL Battery Low / aa: condition code 00 NONE, INACTIVE 11 VALID, ACTIVE

ACxx(cr)(lf) ssss(cr)(lf)	Acknowledgement of variable parameter

B.2 Values (5 character labels)
Title	Description
Mxxxx(cr)(lf) yyyy.yy(cr)(lf)	Measured or present values xxxx: 1st 2nd 3rd -4th / I Input U Voltage (V) PO Positive B Battery I Current (A) NE Negative U Ups P Power (kW) L1,L2,L3 O Output S App. Power (kVA) 01-99 E Environment F Frequency UU,II,FF D Distribution P1,P2,P3 L Link P Bypass 2nd -3rd 4th / TE Temperarure (C) 1-9 CH Charge (%) PF Power factor RH Humidity (%) CO Contact IN Index
Nxxxx(cr)(lf) yyyy.yy(cr)(lf)	Fixed nominal values or range limits xxxx: 1st 2nd 3rd-4th / I Input U Voltage (V) HH High B Battery I Current (A) NN Nominal U Ups P Power (kW) LL Low O Output S App. Power (kVA) PH Peak high E Environment F Frequency D Distribution T Time (min) 2nd-3rd 4th / TE Temperarure (C) H High CH Charge (%) N Nominal PF Power factor L Low RH Humidity (%) AH Capacity (Ah)
BTIME(cr)(lf) yyyy.yy(cr)(lf)	Estimated battery backup time
BDATx(cr)(lf) yQyy (cr)(lf)	Battery installation date, where x = 1…8
NNAME(cr)(lf) yyyy.yy(cr)(lf)	UPS type string

APPENDIX C: UPScode I
An earlier implementation of the UPScode protocol, used in the Powerlink EIU product is a subset of the present UPScode II protocol. UPScode I is simpler and contains less information. The information included in UPScode I corresponds to the data available through the common four relay UPS interface.

C.1 UPScode I interface status (Powerlink EIU compatible)
These messages are included for compatibility with software written for previous UPS interfaces and should not be used in new applications. This is a subset of the information available by using the UPSS command.

The condition of four UPS system signals and four environment contacts is available with this command:

Command	Description
UPST(cr)	STATUS REPORT

The UPS will respond to this command by transmitting:

Status response	Comment
ASON(cr)(lf) aa(cr)(lf)	UPS ON / OK ’00’ UPS OFF - ’11’ UPS ON
ASBP(cr)(lf) aa(cr)(lf)	BYPASS ACTIVE ’00’ UPS ON LINE - ’11’ UPS BYPASSED
ASUF(cr)(lf) aa(cr)(lf)	UTILITY FAILURE ’00’ UTILITY OK - ’11’ BATTERY OPERATION
ASBL(cr)(lf) aa(cr)(lf)	BATTERY LOW ’00’ BATTERY OK - ’11’ BATTERY LOW
MECOx(cr)(lf) aa(cr)(lf)	ENVIRONMENT CONTACT x (1, 2, 3 and 4) ’00’ INACTIVE - ’11’ ACTIVE (Four dummy messages for compatibility with Powerlink EIU unit, always inactive wihout EIU)

Note that in UPScode I, all the above (8) messages are always transmitted.

C.2 Automatic UPScode I messages
In order to ensure compatibility with software written to the UPScode I specification, in some older UPSs, the UPScode I or the UPScode II mode can be selected by setting a DIP switch.

When UPScode I mode is selected, the above messages are sent automatically as the status changes, instead of the messages in 3.1.1. All the UPScode II commands are still valid when issued, but no UPScode II messages (that could confuse existing software) are sent automatically.
APPENDIX D: Revision history

The changes from 1002889 rev G to 1002889 rev H
Added STLR status message condition DU.

Added STAT messages AC, BT, BX, DU, EP, FT, IB, IP, LR, OD, OR, OV, OW, PB, UU, and VE.

Added STEA and STEF status message conditions 01…09.

Added description of UPBS, UPR0 and UPR1 commands.

Added description of UPPM parameter’s P19 value V06.

Added description of UPPM parameters P26, P27, P28, and P29.

Added a list of the reserved UPScode commands in Appendix A.

The changes from 1002889 rev H to 1002889 rev I
Added description of MLUUU measurement in the UPDS dump.

Added description of UPID command.

Changed description of UPPM parameter P28 from ”Paralleling mode” to ”Paralleling enable/disable”. Added parallel unit numbers 3 and 4.

Added description of UPPM parameters P30, P31, and P32.

Added UPDX to the list of the reserved commands.

The changes from 1002889 rev I to 1002889 rev J
Added MIFFF (input frequency) measurement to the UPDS response.

Added description of UPPM parameter’s P13 value V04 (no batteries).

Added description of UPPM parameter’s P00 value V04 (environment alarm).

Changed description of the values of UPPM parameter P32.

Added description of UPPM parameters P33, P34, P35, and P36.